EnergyLens

Dashboard Master Guide

9-Page Power BI Report — Page-by-Page Technical & Energy Engineering Walkthrough

This document walks through every KPI card and visual on each of the 9 pages of the EnergyLens Power BI report: what it shows, how it's computed, how to read it, and why it matters for the building. Intended audience: the product owner / energy domain reviewer, consultants who will eventually use the platform, and facility managers as end-users.

| Platform | EnergyLens — Energy Copilot Platform for Commercial Buildings |
| --- | --- |
| Architecture | Microsoft Fabric (Medallion: Bronze → Silver → Gold) + Power BI |
| Modeling approach | BMAD — Business → Architecture → Data → Logic → Implementation |
| Report version | DAX v42 (Page 7), v44 (Page 8), v47/v48 (Page 9) — 9 pages |
| Portfolio | 6 buildings — Berlin (DE), Hamburg (DE), Frankfurt (DE), Vienna (AT), Amsterdam (NL), Istanbul (TR) |
| Data coverage | 2023-01 → 2026-05, 15-min / hourly energy + solar + battery + occupancy + weather |
| Date | 2026-05-13 |

0. Project at a Glance

Why does it exist?

Commercial buildings are under pressure on three fronts: (1) rising and volatile energy costs, (2) EU and national regulation (EPBD 2030, CSRD, ETS2, CRREM stranding), and (3) net-zero commitments. Existing BMS / SCADA systems are operational but lack the 'financial + compliance + carbon strategy' layer. EnergyLens fills that gap as a decision-support platform — the productisation of the 'energy copilot' concept.

Three user personas

Facility Manager — daily operations, anomaly handling, comfort/IoT (Pages 2, 3, 5, 8)

Energy Manager / Consultant — portfolio KPIs, forecast, retrofit, carbon (Pages 1, 4, 6, 7, 9)

Platform Admin — building onboarding, subscriptions, demos

Architecture summary

Microsoft Fabric Lakehouse with medallion architecture:

Bronze — raw data (CSV, API, IoT sensor, EPEX price, weather)

Silver — cleaned, normalised, standard units (kWh, kW, °C, ppm, tCO₂)

Gold — business logic (gold_kpi_daily, gold_hvac_analytics, gold_battery_dispatch, gold_iot_realtime, gold_compliance_results)

Power BI semantic model is bound to Gold via DirectLake. DAX measures are versioned per page from v34 → v48.

Page map — what does each page answer?

| Page 1 | Portfolio Overview — executive summary (kWh, EUI, anomalies, cost, carbon) |
| --- | --- |
| Page 2 | Energy Profile — daily profile, peak demand, solar, battery, weather signature (HDD/CDD) |
| Page 3 | Anomaly & Risk Monitor — fault detection, severity distribution, resolution speed |
| Page 4 | Forecast & Recommendations — ML forecast + action recommendations + payback |
| Page 5 | Occupancy — usage profile, 7×24 heatmap, after-hours waste |
| Page 6 | Carbon & CRREM — GHG intensity, EPC, ETS2 exposure, stranding year |
| Page 7 | HVAC & Envelope — system types, COP/SCOP, heat loss, retrofit priority |
| Page 8 | IoT Monitoring — real-time kW, zone comfort, sensor health, live alerts |
| Page 9 | Battery Strategy — solar+battery strategies, payback, ROI, 24h dispatch |

Page 1 — Portfolio Overview / Executive Summary

Purpose of the page

When an energy manager or building owner asks 'where do we stand?' in the morning, this is the first screen. The whole portfolio is summarised in 30 seconds. It drives a single decision: which building or issue should I focus on today?

Target users: Energy Manager, Consultant, C-level. No operational detail — this page is the strategic filtering layer.

Top band — KPI cards

C1 — Total Energy Consumed (113,148 kWh)

| What it shows | Total electricity + gas (kWh equivalent) consumption for all buildings in the selected period. |
| --- | --- |
| How it's computed | SUM(gold_kpi_daily[total_consumption_kwh]) — responds to slicer filters. 'Goal' shown below: prior year (PY) or target. |
| How to read it | Absolute magnitude → describes portfolio scale. -5.26% means below target (good). Green arrow. |
| Why it matters | Total consumption is the base figure for the bill. Carbon, cost and EUI depend on it as a denominator — this card is meaningless alone; read it alongside the others. |

C2 — Avg EUI (0.25 kWh/m²/day)

| What it shows | Energy Use Intensity — daily consumption per unit area (kWh / m² · day). The gold-standard metric for comparing buildings. |
| --- | --- |
| How it's computed | AVG(daily_kwh / building_area_m2) — simple mean, not area-weighted. Annualise with ×365. |
| How to read it | 0.25 kWh/m²/day = 91 kWh/m²/year. European office average ~150-250 kWh/m²/year. Portfolio looks efficient overall — but distribution across buildings matters (see EUI Benchmark below). |
| Why it matters | EUI is the size-independent 'efficiency' metric. It is the foundation of EPBD 2030, CRREM and EPC systems. An energy manager speaks in kWh per m². |

C3 — Active Anomalies (12)

| What it shows | Number of currently active (is_resolved = FALSE) anomalies. Total across all severities. |
| --- | --- |
| How it's computed | COUNT(gold_anomaly_alerts WHERE is_resolved = FALSE) — slicer-aware. |
| How to read it | 12 anomalies = low-to-moderate workload. 50+ would be a red flag. Click into Page 3 for severity breakdown. |
| Why it matters | An anomaly is a signal of energy waste or equipment fault. Each one accumulates extra cost while open. Read it together with resolution rate and avg days open (Page 3). |

C4 — Total Energy Cost (€28,958)

| What it shows | Electricity + gas cost for the selected period. |
| --- | --- |
| How it's computed | SUM(daily_kwh × price_per_kwh) — country-based tariffs: DE €0.20/kWh electricity, €0.07/kWh gas; TR €0.14/kWh; etc. Same pricing logic as Page 9. |
| How to read it | Sensitive to both tariff changes and consumption reductions. Never read alone — pair with kWh: did consumption fall, or did the tariff drop? |
| Why it matters | The 'monetary face' for decision-makers (CFO, owner). Engineers speak in kWh, finance speaks in €. EnergyLens makes that translation explicit. |

C5 — Net Carbon Footprint (28 tCO₂)

| What it shows | Net carbon footprint: direct emissions (Scope 1 — gas, boilers) + indirect emissions (Scope 2 — grid electricity) − emissions avoided through solar / green energy. |
| --- | --- |
| How it's computed | Σ(kWh × grid_carbon_intensity g/kWh) + Σ(gas_kwh × 0.20 kgCO₂/kWh) − Σ(solar_kwh × grid_carbon_intensity) |
| How to read it | 28 tCO₂ — beats the goal (79) by -64.42% (good). The target may be aggressive, or consumption has dropped significantly. |
| Why it matters | The foundational number for CSRD and ETS2 reporting. From 2027, EU commercial buildings will fall under ETS2: roughly €85-100 tax per tCO₂. 28 tCO₂ × €100 = €2,800 of additional annual cost. |

Secondary cards (lower band)

Last Week Consumption (8,005 kWh, ▼2.2% WoW) — short-term trend. A weekly drop within normal variance.

Last Month Consumption (▼▼43.5% MoM) — massive monthly drop. Likely seasonal (end of heating season) or building closure — should not be read as 'improvement' on its own; needs HDD/CDD normalisation (Page 2).

Last 7 Days Cost (€1,585.63) and Last 30 Days CO₂ (8.9 tCO₂) — quick sanity checks.

V1 — Building-Based Consumption (Current vs PY)

Visual type: Clustered Column Chart

| What it shows | X-axis = building name; Y = total kWh; two bars per building: Current period vs Prior Year (PY). |
| --- | --- |
| How it's computed | SUM(total_consumption_kwh) by building; PY uses LASTYEAR / DATEADD DAX patterns for the same period. |
| How to read it | Year-on-year comparison per building. Berliner Bürogebäude Alpha 1,381K → 1,251K = -9.4% (good — retrofit or operational improvement). Any building with PY-higher bar is the place to focus. |
| Why it matters | YoY comparison is the only normalised view that accounts for seasonal and operational change. It is insensitive to tariff shifts (in kWh), and carbon/cost move in parallel. |

V2 — Anomaly Severity × Building Heatmap

Visual type: Matrix / Heatmap

| What it shows | Rows = building, columns = Critical / High / Medium / Low; cell = anomaly count; colour saturation by count. |
| --- | --- |
| How it's computed | COUNT(anomaly_alerts) GROUP BY building_id, severity. Default: 1 year or whatever the slicer specifies. |
| How to read it | Berliner = 46 (relatively high but the building is large — not normalised). The severity distribution matters: 0 Critical for Berliner is manageable; 10+ would be urgent. |
| Why it matters | Anomaly count alone is not informative — the profile is. 10 Critical in one building = immediate action; 100 Low = sensitive thresholds, noise. Severity profile reads like a 'health X-ray'. |

V3 — Monthly Energy Trend

Visual type: Line Chart (3 series)

| What it shows | X = month; 3 lines: Total Consumption (current), Total Energy PY (prior year), Energy Reduction Target. |
| --- | --- |
| How it's computed | Monthly aggregation; PY = same month last year (SAMEPERIODLASTYEAR); Target = annual target ÷ 12 or manual slope. |
| How to read it | Seasonal pattern surfaces: winter (Dec-Feb) peak (heating), midsummer (Jul-Aug) secondary peak (cooling). Current below PY = portfolio improving. Current below Target = goal on track. |
| Why it matters | Without weather normalisation, 'consumption up/down' interpretations are misleading. This visual gives the year-long continuity feel, especially read with PY and Target. |

V4 — EUI Benchmark by Building

Visual type: Horizontal Bar

| What it shows | Y = building name; X = EUI (kWh/m²/day); reference line: portfolio average or climate-zone benchmark. |
| --- | --- |
| How it's computed | AVG(daily_kwh / area_m2) by building_id. Annualise with ×365. |
| How to read it | Berliner ~0.24 (modern building, good envelope); Frankfurt Klinikum is higher (24/7 hospital with fan + sterilisation load). High EUI ≠ bad; know the building type. |
| Why it matters | The only apples-to-apples metric for building comparison. Use it within building type (office vs office). It is the basis of EPC and CRREM benchmarks. |

Map (TomTom)

Geographic distribution of buildings. The geographic cluster (DE 4, NL 1, TR 1, AT 1) tells the market-density and operational geography story. In a client pitch it conveys a 'pan-European portfolio' feel.

How to talk about this page (consultant pitch)

In one sentence: 'Our portfolio is 6 buildings, 113K kWh monthly consumption, EUI 91 kWh/m²/year — below the European office average. 28 tCO₂ monthly net carbon and 12 active anomalies. Berliner Bürogebäude Alpha makes up ~30% of the portfolio and is down -9% YoY — operational improvement or a retrofit effect.' That sentence sells in 30 seconds to a CFO/owner.

Page 2 — Daily Consumption / Energy Profile

Purpose of the page

Where Page 1 is strategic, Page 2 is operational — the page a facility manager checks daily. How is the building living: when does it peak, is there a weather effect, what is solar/battery contributing?

Target users: Facility Manager + Energy Engineer. This page is the 'observation' layer that comes before any ML forecasting.

Top band — KPI cards

Daily Consumption (kWh)

| What it shows | Total consumption for the latest or selected day. |
| --- | --- |
| How it's computed | SUM(total_consumption_kwh) WHERE date = MAX(date) — depends on the slicer date. |
| How to read it | If you see '(Blank)' either there's no data for that date or the slicer is on All and the latest data hasn't been pushed through bronze→silver yet. Goal: 5,928 — actual is 0 → ETL gap. |
| Why it matters | Daily consumption is part of the bill alongside peak demand (especially in demand-charge tariffs). |

Peak Demand (kW)

| What it shows | The highest 15-minute average power draw in the selected period. |
| --- | --- |
| How it's computed | MAX(15min_avg_kw) — sliding window MAX on the Power BI side; needs 15-minute aggregation from raw data. |
| How to read it | Peak demand drives the 'demand charge' portion of the bill (DE €13.50/kW/month, NL €14.80/kW/month — see Page 9). A single hourly peak pushes the month's bill up. |
| Why it matters | It is the foundational metric for peak shaving (battery) and load shifting (HVAC scheduling) strategies. A -50 kW peak shave in DE = ~€8K annual saving. |

EUI (kWh/m²) — 0.68

| What it shows | Daily energy use per unit area — the daily version of Page 1's EUI. |
| --- | --- |
| How it's computed | daily_kwh / building_area_m2 |
| How to read it | 0.68/day → 248 kWh/m²/year — high. Either a one-off spike or the selected building is high-load (hospital, hotel). |
| Why it matters | Daily EUI volatility shows how stable building operations are. If the same building has EUI 0.68 on Monday and 0.30 on Sunday — that's occupancy-driven and normal. |

Solar Generation (kWh)

| What it shows | Total energy generated by the PV system (selected period). |
| --- | --- |
| How it's computed | SUM(solar_generation_kwh) FROM gold_solar_generation |
| How to read it | '(Blank)' means no PV or a pipeline error. B005 Frankfurt 200 kWp, B003 Hamburg 500 kWp — the large producers. |
| Why it matters | Discount line in net carbon and cost calculations. The self-consumption ratio matters: solar generated but exported back to grid is at a different tariff. |

Battery SoC (60.4%)

| What it shows | Battery state of charge. |
| --- | --- |
| How it's computed | AVG(soc_percent) WHERE timestamp = MAX(timestamp). Range 0-100%. |
| How to read it | 60% — healthy mid-range; staying between 20-80% is ideal for battery longevity (low deep-cycle damage). If it never reaches 95%+ or drops below 5%, the strategy is working efficiently. |
| Why it matters | SoC is the real-time state of the dispatch strategy (Page 9). In a peak-shaving strategy, SoC should be 80%+ before the evening peak. |

Carbon Intensity (kgCO₂/m²)

| What it shows | Carbon emissions per unit area — the carbon version of EUI. |
| --- | --- |
| How it's computed | (total_kwh × grid_g_co2_per_kwh + gas_kwh × 200 g/kWh) / area_m2 / 1000 |
| How to read it | Critical metric for CRREM stranding and EPC. EU 2030 office target: 20-30 kgCO₂/m²/year. Buildings above that risk being 'stranded assets'. |
| Why it matters | Carbon intensity is the foundational number for EU Taxonomy and green certification. EUI may be high while carbon intensity is low (PPA + solar) — the real measure of a 'green building'. |

V1 — Consumption + Temperature + 7-Day Avg

Type: Combo Chart (line + secondary axis)

| What it shows | Blue line: Total Consumption kWh (left Y); orange line: 7-Day Rolling Avg; grey line: Avg Temperature °C (right Y). |
| --- | --- |
| How it's computed | 7-day rolling avg = AVERAGEX over -3 to +3 days. Temperature from gold_weather_daily via DirectLake. |
| How to read it | Consumption and temperature show inverse/direct correlation: winter T ↓ → consumption ↑ (heating); summer T ↑ → consumption ↑ (cooling). The 7-day avg removes noise to reveal the true trend. |
| Why it matters | Without weather normalisation (HDD/CDD), the consumption trend can show 'false positive' improvements. Seasonality normalised, the real operational change becomes visible. |

V2 — EUI Gauge

Type: Radial Gauge

| What it shows | Min: 0, Target: 0.27, Max: 1.00. Current 0.27 → red 'Poor' (target exceeded). |
| --- | --- |
| How it's computed | Single value: AVG(daily_eui). Threshold colours defined in DAX (green <0.20, amber 0.20-0.27, red >0.27). |
| How to read it | The gauge tells you whether the target is met but loses context — the true picture is in the annual trend. This visual answers 'where are we right now'. |
| Why it matters | Gauges have strong marketing appeal but are misleading alone — always read alongside a trend visual. |

V3 — Solar Self-Consumed vs Exported vs Grid

Type: Stacked Area Chart

| What it shows | Three areas: Solar Self-Consumed, Solar Exported (sold back to grid), Total Grid Consumption (bought from grid). |
| --- | --- |
| How it's computed | self_consumed = MIN(solar_gen, consumption); exported = solar_gen - self_consumed; grid = consumption - self_consumed |
| How to read it | High self-consumption — PV sized correctly, fast amortisation. High exported — you're selling cheap (DE feed-in ~€0.08/kWh, retail ~€0.30/kWh) — add a battery to self-consume more. |
| Why it matters | The accuracy of PV sizing decisions shows here. 'Solar-to-self-consumption %' = self_consumed / (self_consumed + exported) — target ≥70% as a KPI. |

V4 — Battery SoC Trend %

Type: Line Chart

| What it shows | X = month/day; Y = average SoC %. |
| --- | --- |
| How it's computed | AVG(soc_percent) GROUP BY date or month. |
| How to read it | A very flat line (e.g. constant 60%) = battery idle, not being used. A volatile line (cycling between 20-80%) = active dispatch. Constantly 95%+ = strategy isn't engaging (as in Backup-only strategies). |
| Why it matters | Battery investment amortises only with active usage. An idle battery = frozen capital. This visual is the test of whether the strategy is working. |

Live Building Power + Live HVAC Load

Live Building Power: 111 kW, Live HVAC Load: 50 kW. The last 15-minute average draw. HVAC share = 50/111 = 45% — high, a sign of winter or hot weather (cooling). This pair aligns with Page 7's HVAC Share Pct as a 'right-now' snapshot.

V5/V6 — HDD vs Consumption & CDD vs Consumption (Scatter)

Type: Scatter (each point = a month)

| What it shows | X = Heating Degree Days (HDD) or Cooling Degree Days (CDD); Y = monthly kWh. |
| --- | --- |
| How it's computed | HDD = Σmax(0, 18°C − T_avg_daily); CDD = Σmax(0, T_avg_daily − 22°C). Monthly totals. |
| How to read it | Slope of the correlation line = building's heating/cooling sensitivity. Steep slope = weak envelope (each extra HDD costs many extra kWh). Shallow slope = good insulation or efficient HVAC. |
| Why it matters | The visual form of the 'baseline regression' technique in energy engineering. It is the foundation of pre/post retrofit comparison in M&V (Measurement & Verification, IPMVP Option C) projects. |

How to talk about this page

'The building peaks at about 111 kW, with HVAC taking ~45%. After weather normalisation (HDD/CDD scatter), the true YoY trend is -9%. Our solar self-consumption ratio is X% — a battery investment could push it to 90%+, with payback Y years (cross-ref to Page 9).'

Page 3 — Anomaly Detection & Risk Monitor

Purpose of the page

The Fault Detection & Diagnostics (FDD) page. Which building has what type of anomaly, how many are critical, how long have they been open? An energy manager uses it as an 'operational health dashboard'.

Anomaly types: CONSUMPTION_SPIKE, SOLAR_UNDERPERFORM, AFTER_HOURS_WASTE, HIGH_CARBON_INTENSITY. Rule-based today, not ML — adaptive ML will be added in Phase 2.

Top band — KPI cards

Total Anomalies (582)

| What it shows | Total anomalies detected in the selected period (resolved + unresolved). |
| --- | --- |
| How it's computed | COUNT(gold_anomaly_alerts) — responds to slicers. |
| How to read it | 582 alone is not meaningful — over 1 year it's low, over 1 month it's high. If most are Low/Medium, threshold sensitivity is tight (lots of noise); if mostly Critical, real issues exist. |
| Why it matters | Anomaly count ≠ energy waste. What matters is how many are resolved and how many carry a € cost. |

Critical Anomalies (51 / Open)

| What it shows | Critical-severity anomalies that are open (is_resolved = FALSE). |
| --- | --- |
| How it's computed | COUNT WHERE severity = 'CRITICAL' AND is_resolved = FALSE |
| How to read it | 51 open critical = immediate action required. Critical = energy waste + likely equipment fault + potential EU compliance risk (e.g. EPC drift). |
| Why it matters | Pairs with 'CRITICAL Actions' on Page 4. Each critical anomaly produces a recommended action; that list lives on Page 4. |

High Anomalies (158)

| What it shows | All High-severity anomalies (resolved + unresolved). |
| --- | --- |
| How it's computed | COUNT WHERE severity = 'HIGH' |
| How to read it | High > Critical ratio (158 vs 51 ≈ 3:1) is healthy — a pyramid shape: few critical, more high, even more low. |
| Why it matters | Severity distribution is a 'sensitivity calibration' problem. Too many critical = thresholds are too tight, false positives are high. The severity profile is a calibration job. |

Unresolved (582) & Active Anomaly Rate %

| What it shows | Open (resolved = FALSE) count + the share they represent. |
| --- | --- |
| How it's computed | Rate = unresolved / total × 100 |
| How to read it | Currently 100% unresolved — that's an ETL bug (is_resolved always FALSE). Pending fix in Notebook 29b. Real-world rates are typically 20-40%. |
| Why it matters | Resolution rate reflects an operational team's maturity. 80%+ = active team; 30% or less = anomalies pile up, the system loses signal. |

V1 — Operational Fault Detection & Risk Monitor (Table)

Type: Table

| What it shows | Columns: Building, Severity, Anomaly Type, Detected (timestamp), Deviation %, is_resolved. |
| --- | --- |
| How it's computed | gold_anomaly_alerts joined with silver_building_master[building_name]. |
| How to read it | Deviation % = how far the anomaly drifted from baseline. CONSUMPTION_SPIKE 10% = 10% above expected (meaningful drift). >15% is usually Critical. |
| Why it matters | This is the FM's work list. Sort by severity, prioritise oldest open items (high avg days open = no clear owner). |

V2 — Monthly Anomalies by Severity (Stacked Column)

Type: Stacked Column

| What it shows | X = month; Y = count; stack: CRITICAL / HIGH / MEDIUM / LOW. |
| --- | --- |
| How it's computed | COUNT GROUP BY YearMonth, severity |
| How to read it | Look for seasonality. Rising critical in winter = heating systems faulty. Summer peaks = HVAC chiller anomalies. March-April lull = season transition. |
| Why it matters | Anomaly timing is a clue to which system has the issue. Monthly series are for 'seasonal pattern detection'. |

V3 — Anomaly Type Breakdown (Horizontal Bar)

Type: Horizontal Bar

| What it shows | Four types shown: SOLAR_UNDERPERFORM (319), AFTER_HOURS_WASTE (172), HIGH_CARBON_INTENSITY (81), CONSUMPTION_SPIKE (10). |
| --- | --- |
| How it's computed | COUNT GROUP BY anomaly_type |
| How to read it | SOLAR_UNDERPERFORM dominates — PV soiling / inverter fault / shading. AFTER_HOURS_WASTE second — HVAC or lighting on overnight / weekends. CONSUMPTION_SPIKE only 10 — few large swings. |
| Why it matters | The anomaly-type distribution tells you what work to do: a lot of SOLAR_UNDERPERFORM → O&M contract or panel cleaning; a lot of AFTER_HOURS_WASTE → BMS scheduling fault or occupancy mis-set (cross-ref Page 5). |

V4 — Building Anomaly Share (% of portfolio)

Type: Horizontal Bar

| What it shows | Y = building; X = building anomaly count / portfolio total × 100. |
| --- | --- |
| How it's computed | (COUNT per building / SUM all) × 100 |
| How to read it | Istanbul 36.4%, Frankfurt 18.7%, Amsterdam 17.4%, Berlin 11%. Istanbul's share is high — either the building has issues, or thresholds aren't calibrated for the climate. |
| Why it matters | Anomaly share doesn't equal 'problem building' — unless area-normalised, larger buildings produce more anomalies. Still, a single building at >30% is a red flag. |

Lower band — Resolution / Risk Score cards

| Resolution Rate % | Resolved / total × 100. Currently --- (ETL bug). Target ≥70%. |
| --- | --- |
| Avg Days Open (732) | Average age of open anomalies. 732 days ≈ 2 years — artificially high because the fix never reaches the data. |
| High Priority Open Count (209) | Open High + Critical count. The team's workload. |
| Top Risk Building Score (Istanbul: 212) | Risk score = critical_count × 4 + high × 2 + medium × 1; Istanbul tops the list. |

How to talk about this page

'The portfolio has 582 anomalies, ~35% in Istanbul. The biggest issue area is SOLAR_UNDERPERFORM — that costs us about €X/month. AFTER_HOURS_WASTE is also significant — BMS scheduling and occupancy mismatch (provable from Page 5). Resolution rate is low; recommendation: assign anomalies to the FM team under an SLA.'

Page 4 — Forecast & Recommendations

Purpose of the page

Forecast (ML) + Action recommendations (rule-based + ML hybrid). It answers 'what will happen in the next N days, and what should we do about it?'. This is the 'work generation' page for energy managers and consultants.

Top band — KPI cards

7-Day Forecast (10,766 kWh)

| What it shows | Forecast total consumption for the next 7 days. |
| --- | --- |
| How it's computed | ML model (07_consumption_forecast.py — XGBoost / Prophet) hourly forecast → 7-day total. |
| How to read it | vs PY: Goal 8,012 (+34%) — so we expect higher consumption next week. Could be a cold-weather forecast, a new tenant, or operational change. |
| Why it matters | Short-term forecast is critical for demand-response participation. Day-ahead forecast accuracy enables bill optimisation. |

30-Day Forecast (44,163 kWh)

| What it shows | Forecast for the next 30 days. |
| --- | --- |
| How it's computed | Same model, 30-day horizon. Wider confidence interval. |
| How to read it | Used for monthly bill forecasting. Target accuracy ±5%. |
| Why it matters | Monthly budget forecast is critical for the finance team. Cash flow planning depends on this number. |

Savings Potential (€)

| What it shows | Total annual € savings from action recommendations. |
| --- | --- |
| How it's computed | SUM(recommendation_annual_savings_eur) — per-recommendation savings summed. |
| How to read it | (Blank) — the recommendation engine isn't bound to buildings yet. Goal: 300K — aggressive. Expected real range: 100-200K. |
| Why it matters | The monetary value of recommendations is the basis of the sales pitch: 'the platform earns you €X annually'. The backbone of ROI presentations. |

CRITICAL Actions (8)

| What it shows | Count of recommendations that require immediate attention. |
| --- | --- |
| How it's computed | COUNT WHERE recommendation_priority = 'CRITICAL' |
| How to read it | 8 critical actions = this week's must-do list. Different from Page 3's 51 critical anomalies — not every anomaly creates a recommendation; each recommendation may roll up several anomalies. |
| Why it matters | The work list. Consultants say 'do these this week' — this card is the short version of that list. |

Avg MAPE %

| What it shows | Mean Absolute Percentage Error — average forecast accuracy. |
| --- | --- |
| How it's computed | MAPE = AVG(¦actual - forecast¦ / actual × 100). On a hold-out test set. |
| How to read it | <10% — excellent; 10-20% — acceptable; >20% — model unfit. Goal: 10 (-22%) — below target. |
| Why it matters | The measure of model trust. Don't make investment decisions on a high-MAPE forecast. This number tells you whether the model is 'production ready'. |

V1 — Monthly Consumption — Actual & Forecast (Line)

Type: Line Chart, 3 series

| What it shows | Actual kWh (solid blue), Forecast kWh (dashed red), PY kWh (grey). |
| --- | --- |
| How it's computed | Actual = SUM(daily) GROUP BY month; Forecast = ML output; PY = SAMEPERIODLASTYEAR. |
| How to read it | The forecast line should be a smooth continuation of actual — historical consistency. If forecast diverges significantly from PY, an anomaly is expected (growth or contraction). |
| Why it matters | The forecast visual gives clients a 'you're in control' feeling. It's the strongest visual in a sales demo. |

V2 — Recommendations Table

Type: Table

| What it shows | Columns: Building, Recommendation, Priority, Total Annual Saving EUR, Payback (years). |
| --- | --- |
| How it's computed | gold_recommendations table (notebook 06_recommendation_engine.py) — rule-based recommendation engine. |
| How to read it | Examples: 'Implement HVAC Scheduling' HIGH, €20,880/yr. 'Optimise Building Management' HIGH, €30,933/yr — highest value. 'Upgrade to LED Lighting' LOW, €16K — easy quick win. |
| Why it matters | The recommendation list is the consultant's 'sell to client' work map. Sorted by Priority + Payback, it becomes a project plan. |

V3 — Payback vs Savings (Scatter)

Type: Scatter

| What it shows | X = Payback (years), Y = Annual Savings (€); each point = a recommendation; colour/shape = Priority. |
| --- | --- |
| How it's computed | Direct join to the recommendations table. |
| How to read it | Top-left (short payback + high savings) = quick wins, do first. Bottom-right (long payback + low savings) = defer or skip. Bottom-left = low impact but fast (cosmetic). |
| Why it matters | Also known as an ROI matrix. A common language between engineers and finance — 'payback under 5 years = approve'. |

V4 — Actions by Priority (Bar)

Type: Bar Chart

| What it shows | X = count; Y = HIGH/MEDIUM/LOW. |
| --- | --- |
| How it's computed | COUNT GROUP BY priority |
| How to read it | Balanced 2-2-2 distribution — healthy. Mostly LOW = missing quick wins; mostly HIGH = team overload. |
| Why it matters | Balance of the action portfolio — a maturity indicator for the sustainability programme. |

V5 — MAPE Accuracy by Building

Type: Bar with threshold

| What it shows | Y = building; X = MAPE %; threshold line: 10% (Excellent/Poor boundary). |
| --- | --- |
| How it's computed | MAPE calculated per building. |
| How to read it | Berliner Bürogebäude Alpha: 7.8% — Excellent. Any building above 20% needs the model retrained (different season pattern, missing feature). |
| Why it matters | Per-building MAPE tests whether the model generalises. If one model predicts 6 buildings 'in one hand', building_id should be one-hot encoded or per-building models trained. |

How to talk about this page

'We expect 44K kWh consumption in 30 days, +X% vs last year. The HVAC Scheduling recommendation for the client saves €21K/year with a 3-year payback. Combine it with Building Management optimisation and we're at €50K+/year saved — they'd recover the investment in 18 months. Our model accuracy is MAPE 8% — production-grade.'

Page 5 — Occupancy / Operations Profile

Purpose of the page

When is the building occupied, when is it empty — and how does energy consumption track that? Without occupancy data, after-hours waste can't be detected. This page shows the building's rhythm.

Data source: badge access, BMS occupancy sensors, manual calendar. In EnergyLens, currently profile-based (synthesised from schedule + Wi-Fi).

Top band — KPI cards

Avg Occupancy Rate (34.7%)

| What it shows | Average occupancy across all hours. |
| --- | --- |
| How it's computed | AVG(occupancy_pct) over ALL hours/days |
| How to read it | 34.7% — looks low, but it's a 24/7 mean so that's right. During business hours it's 70%+; at night ~5%; the mean checks out. |
| Why it matters | Low occupancy affects sizing decisions: 'hot desking, floor consolidation' recommendations come from here. |

Peak Occupancy Hour (14:00)

| What it shows | Busiest hour of the day. |
| --- | --- |
| How it's computed | Hour MAX(occupancy_pct) |
| How to read it | 14:00 — early afternoon peak (post-lunch return + heavy meeting block). Typical Mon-Fri pattern. |
| Why it matters | Does peak occupancy align with peak demand? The comparison reveals load shifting opportunities. |

After-Hours Occupancy (%) — 48

| What it shows | Average occupancy outside working hours (18:00-08:00). |
| --- | --- |
| How it's computed | AVG(occupancy_pct) WHERE hour NOT IN (08-18) AND day IN (Mon-Fri) |
| How to read it | 48% — suspiciously high. Either a night shift (hospital B005?) or sensor misinterpretation. Goal: 45 — slightly above. |
| Why it matters | High after-hours occupancy means HVAC schedules aren't recalibrated — a sign of energy waste (correlates with AFTER_HOURS_WASTE anomalies). |

Energy / Occupant (kWh/mo)

| What it shows | Monthly consumption per occupant. |
| --- | --- |
| How it's computed | Monthly_kwh / avg_monthly_occupants |
| How to read it | (Blank) — occupant count not yet bound to the building. Goal: 650 kWh/person/month — reasonable for European offices. |
| Why it matters | Per-occupant consumption ties employee experience to cost: an intersection point for HR and sustainability reporting. |

V1 — 7×24 Occupancy Heatmap

Type: Heatmap (day × hour)

| What it shows | Rows: Mon-Sun; Columns: 0:00-23:00; cells: mean occupancy % (dark green = high). |
| --- | --- |
| How it's computed | AVG(occupancy_pct) GROUP BY DayName, Hour |
| How to read it | Weekday 8-18 at 55-76% (peak 14:00 76%); weekend 12-32% (decreasing but present). Mon 17% → Tue 17% → ... too flat: calendar is simulated; in reality there'd be more variation. |
| Why it matters | This heatmap shows the building's biorhythm. HVAC schedules should be calibrated against this pattern. Weekend 32% is still elevated — the HVAC isn't fully shutting down. |

V2 — Hourly Occupancy (Weekday vs Weekend)

Type: Line Chart, 2 series

| What it shows | X = hour (0-23); Y = avg occupancy %; two lines: Weekday, Weekend. |
| --- | --- |
| How it's computed | AVG GROUP BY hour, is_weekend flag |
| How to read it | Weekday shows a clear trapezoid (8-18); Weekend stays low and flat. The gap between them = the 'idle but heated/cooled' duration. If the weekend line doesn't reach 0, the system isn't shutting down at weekends. |
| Why it matters | The gold standard visual for setting system schedules. HVAC, lighting, and ventilation should be 'occupancy modulated' (DCV — demand controlled ventilation). |

V3 — Building Avg Occupancy Comparison

Type: Horizontal Bar

| What it shows | Y = building; X = mean occupancy %. |
| --- | --- |
| How it's computed | AVG GROUP BY building |
| How to read it | Frankfurt Klinikum 52.5 (hospital, 24/7, naturally high); Wien Grand Hotel 49.4 (hotel — busy); Berliner 25.9; Amsterdam 20.5 (university — summer empty). Sensible distribution. |
| Why it matters | Without normalising for building type, a 'this building is full/empty' interpretation is invalid. Don't compare a hotel against an office. |

How to talk about this page

'During weekdays the building is 70%+ occupied 8-18, but at weekends 30% 'idle occupancy' means HVAC isn't fully shutting down — this is €X/month of AFTER_HOURS_WASTE (consistent with Page 3 anomalies). Schedule fix recommendation: drop weekend HVAC by 25%, 6-month payback.'

Page 6 — Carbon Compliance / CRREM

Purpose of the page

The carbon and regulation page. CRREM (Carbon Risk Real Estate Monitor), EPC, ETS2, and EPBD 2030 targets. It answers a building owner's questions: 'Will I be legally stranded by 2030? How much will I pay under ETS2?'

CRREM is the most widely adopted carbon-pathway standard for EU commercial real estate. It sets a per-asset annual pathway target; buildings that exceed it become 'stranded assets' (hard to resell).

Top band — KPI cards

GHG Intensity (23.2 kgCO₂/m²/yr)

| What it shows | Annual carbon emissions per unit area — the central CRREM and EPC metric. |
| --- | --- |
| How it's computed | (elec_kwh × grid_g_co2 + gas_kwh × 200 g) / area_m2 / 1000 |
| How to read it | 23.2 — well below the EU office average (40-60). Solar + low gas use must be at play. CRREM 2030 target ~25 kgCO₂/m²/year — currently below it. |
| Why it matters | This single number is the basis of EU Taxonomy alignment. <30 = green, 30-60 = transition, >60 = stranded risk. |

EPC Portfolio Grade (A+)

| What it shows | Energy Performance Certificate — building energy class (A++/A+/A/B/C/D/E/F/G). |
| --- | --- |
| How it's computed | Combination of annual EUI + GHG intensity + envelope score. Country-calibrated thresholds (DE/AT/NL/TR differ). |
| How to read it | A+ — portfolio in the top class. Meets the EU Taxonomy 'green building' criterion. Critical for attracting investment and commanding premium rent. |
| Why it matters | EPBD 2030: all EU buildings must reach at least class E (committee decision 2024). Lower-EPC buildings cannot be rented or sold from 2030 onward. |

Renewable Energy Share (3%)

| What it shows | Share of total consumption from renewable sources (PV self-consumed + green tariff). |
| --- | --- |
| How it's computed | (solar_self_consumed + green_grid_kwh) / total_kwh × 100 |
| How to read it | 3% — low. Goal: 40 (-92%) — aggressive target, far off. PV self-consumption is low or PV is undersized. Battery + PV expansion needed. |
| Why it matters | The 'green ratio' is critical in EU Taxonomy and CSRD reporting. Investor question: 'how green is your asset'. |

CO₂ Carbon Levy (€138,504)

| What it shows | Expected annual carbon tax — ETS2 (emissions trading for buildings, starting 2027). |
| --- | --- |
| How it's computed | tCO₂ × ETS2_price_eur_per_tco2 (2027 ~€45, 2030 projection €85-130/tCO₂) |
| How to read it | €138K/year — material at portfolio scale. Goal: 176K — below target. As carbon falls, the levy falls too. |
| Why it matters | ETS2 is a legal cost from 2027 on EU buildings. Projected savings here are a core element of an investment decision (e.g. heat pump retrofit). |

CRREM Stranding Year (2026)

| What it shows | The year this building's GHG intensity will exceed the CRREM pathway target. |
| --- | --- |
| How it's computed | First year WHERE current_intensity > crrem_pathway_target. Pathway uses the 1.5°C trajectory linear-falling to 2050. |
| How to read it | 2026 — now! Red-flag urgency. Stranding = non-Taxonomy-aligned asset, harder to refinance, at risk of losing tenants. |
| Why it matters | The CRREM year is the deadline for an investment decision. It means: 'you have until year X to get to Y kgCO₂'. |

V1 — Carbon Intensity vs CRREM Pathways

Type: Multi-Line Chart

| What it shows | X = year; Y = GHG intensity kgCO₂/m²; lines: the building itself, CRREM 1.5°C Pathway, CRREM 2.0°C Pathway, CRREM Benchmark. |
| --- | --- |
| How it's computed | Building values from historical data; pathway targets from the official CRREM dataset (updated annually). |
| How to read it | Building line below the pathway = compliant; the year they cross = stranding year. Reducing slope requires retrofit. |
| Why it matters | This visual is the spine of an investment-analysis pitch: 'we're here today, we need to be here by 2030, without X retrofit we'll be stranded in year Y'. |

V2 — CRREM Status by Building (Table)

Type: Table with status icons

| What it shows | Columns: Building, GHG Intensity, CRREM Carbon Benchmark, CRREM Status. |
| --- | --- |
| How it's computed | Status = compare intensity vs benchmark; icon: 🔴 Stranded / 🟡 Approaching / 🟢 Well Below. |
| How to read it | Istanbul Ticaret Merkezi: GHG 77.5, benchmark 42.4 → 🔴 Stranded Asset. Berliner: 23.7, benchmark 39.5 → 🟢 Well Below. Hamburg: 47.4, benchmark 58.6 → 🟢 Well Below. |
| Why it matters | Action prioritisation per building. Stranded buildings are investment priorities — the rest can hold current performance. |

V3 — Renewable vs Grid Energy Split (Stacked %)

Type: Stacked %

| What it shows | X = month; Y = %; colours: Solar Generated %, Grid Consumption %. |
| --- | --- |
| How it's computed | Monthly shares; solar / (solar + grid) × 100 |
| How to read it | Solar share rises in summer (long days, high yield); grid dominates in winter. Seasonal pattern expected. |
| Why it matters | This visual tells the 'self-sufficiency' story. 30%+ annual solar share is acceptable for an EU Taxonomy 'green' investment. |

V4 — Building Carbon Intensity Comparison (Bar)

Type: Horizontal Bar

| What it shows | Y = building; X = kgCO₂/m²; colour thresholds applied. |
| --- | --- |
| How it's computed | Annual mean GHG intensity per building. |
| How to read it | Frankfurt 0.547 (high — hospital, gas boiler); Istanbul 0.214; Wien 0.143; Hamburg 0.100; Berlin 0.067; Amsterdam 0.050. Ordering correlates with HVAC type (gas boiler = high). |
| Why it matters | The ordering answers 'which building to decarbonise first'. Frankfurt with a heat pump retrofit could see 60% reduction. |

V5 — CO₂ Emission Trend (Annual)

Type: Combo Bar+Line

| What it shows | Bars: Total CO₂ Emissions (tCO₂), Net Carbon Footprint; Line: Total CO₂ Savings. |
| --- | --- |
| How it's computed | Annual aggregate; savings = avoided emissions (solar, retrofit). |
| How to read it | 2023-2026 trend: emissions falling while savings rise — a positive curve. Goal: net-zero by 2050. |
| Why it matters | The strongest visual for narrative: 'we were here, we are here now, we're on the right path.' |

Lower band — Priority Actions & Incentives

ETS2 exposure, EU grants (KfW DE, SDE++ NL, etc.) and compliance status. Currently 'Critical — immediate action required' — drives to the Page 4 action list.

How to talk about this page

'Our portfolio GHG intensity is 23.2 kgCO₂/m²/year — at the EU Taxonomy green threshold. But Istanbul is a stranded asset; CRREM target exceeded by 35 kgCO₂. Frankfurt hospital is also at risk because of gas boilers — the heat pump retrofit recommendation saves €Y/year on ETS2 + €Z/year on energy with a 7-year payback.'

Page 7 — HVAC & Building Envelope

Purpose of the page

A building's energy consumption is 30-60% HVAC + heat losses. This page surfaces system type (heat pump, gas boiler, district, VRF), efficiency (COP/SCOP), envelope (U-value, insulation score) and retrofit prioritisation.

Target users: Energy Engineer, Mechanical Engineer, Asset Manager. Retrofit investment decisions start here.

Top band — KPI cards

HVAC Share Pct (19.9%)

| What it shows | Share of total building energy consumed by HVAC. |
| --- | --- |
| How it's computed | SUM(hvac_kwh) / SUM(total_kwh) × 100 |
| How to read it | 19.9% — low (usually 30-50%). Either good envelope + efficient system (heat pump) or HVAC sub-metering is incomplete. |
| Why it matters | High HVAC share → retrofit priority. Low share → plug load or lighting are the bigger opportunity. |

HVAC Efficiency (51/100)

| What it shows | HVAC system efficiency score — a combination of COP/SCOP, system age, and control quality. |
| --- | --- |
| How it's computed | Weighted: 50% COP_actual_vs_rated, 30% age_factor, 20% control_score |
| How to read it | 51 — moderate-to-low. 'Low — Retrofit' label. Gas-boiler-heavy portfolio pulls this score down; converting to heat pumps would lift it past 70. |
| Why it matters | The efficiency score is the business case for retrofit. Below 60, retrofit ROI typically clears the threshold. |

Avg Insulation Score (72/100)

| What it shows | Envelope (wall, roof, window) insulation score. |
| --- | --- |
| How it's computed | Weighted: 40% wall U-value, 30% roof U-value, 30% window U-value (lower U = better insulation). |
| How to read it | 72 — 'EPC C / Improvement zone'. Berliner 90+ (modern); Amsterdam <50 (old). Higher score = lower U-value = less heat loss. |
| Why it matters | Envelope retrofit (external insulation, double/triple glazing) usually pays back in 15-25 years — long, but EPC class rises and building value increases. |

Heat Loss Annual (29 kWh/m²·yr)

| What it shows | Annual heat loss density — the direct measure of envelope quality. |
| --- | --- |
| How it's computed | U_avg × ΔT_avg × hours / 1000 → kWh/m²/year |
| How to read it | 29 — 'Passive House Level' (<30 kWh/m²/year). Passive house standard — excellent. Low heat loss = low heating demand. |
| Why it matters | Passive house level: the key threshold for PHPP (Passive House Planning Package) certification. EUI and carbon gains follow naturally. |

HVAC CO₂ (3100.2 tCO₂/yr)

| What it shows | Annual HVAC-related emissions (Scope 1 + Scope 2). |
| --- | --- |
| How it's computed | Σ(hvac_gas_kwh × 200 g) + Σ(hvac_elec_kwh × grid_g_co2) |
| How to read it | Scope 1 (gas, direct) ~6%, Scope 2 (electricity, indirect) ~94%. Frankfurt gas boiler is the biggest contributor (1.7M kgCO₂). |
| Why it matters | Scope 1 decarbonisation is the prime target — gas → heat pump means Scope 1 → 0; Scope 2 declines as the grid greens up. |

Buildings For Retrofit (2)

| What it shows | Count of buildings with high retrofit priority. |
| --- | --- |
| How it's computed | COUNT WHERE renovation_priority IN ('Urgent', 'High') |
| How to read it | 2 urgent + 1 planned + 3 (other) — 2 of 6 buildings are priority. |
| Why it matters | The immediate-action list. The starting point for capital planning. |

V1 — HVAC Energy Breakdown by Month

Type: Stacked Column %

| What it shows | X = month; Y = %; stack: Heating / Cooling / Ventilation. |
| --- | --- |
| How it's computed | hvac_kwh decomposition (sub-metering or signature-based). |
| How to read it | Winter (Dec-Feb) Heating 70%+; Summer (Jul-Aug) Cooling dominant; Ventilation ~10-15% steady year-round. Classic HVAC profile. |
| Why it matters | This visual is gold for the HVAC system-selection engineer. In a heating-heavy building, a heat pump at COP=3+ delivers ~70% electricity savings. |

V2 — Building HVAC System Summary (Table)

Type: Table

| What it shows | Columns: Building, System (Heat Pump / Gas Boiler / District / VRF), Priority, COP/SCOP. |
| --- | --- |
| How it's computed | silver_building_master[primary_hvac_system] + COP actual or rated. |
| How to read it | Amsterdam VRF (good for cooling-heavy, low priority); Berliner Heat Pump ASHP (modern, low); Frankfurt Gas Boiler — CSRD warning + 🔴 High; Hamburg Gas Boiler + medium. |
| Why it matters | This table is the spine of a retrofit roadmap. Gas-boiler buildings should convert to heat pumps before 2030. |

V3 — HVAC CO₂ Emissions — Scope 1 vs Scope 2

Type: Stacked Bar

| What it shows | Y = building; X = kgCO₂; stack: Scope 1 (Fossil — gas) / Scope 2 (Electric — grid). |
| --- | --- |
| How it's computed | Same split applied to HVAC. |
| How to read it | Frankfurt Klinikum 1.7M kgCO₂ — almost entirely Scope 1 (gas boiler). Berliner mostly Scope 2 (heat pump, which falls as the grid greens up). |
| Why it matters | Scope 1 = directly controllable; decarbonise here first (fuel switch); Scope 2 = grid-dependent, addressed via PPA + green tariff. |

V4 — Annual Heat Loss Density + Insulation Score by Building

Type: Dual-Axis Bar

| What it shows | Y = building; X1 = Heat Loss kWh/m²/year; X2 = Insulation Score (0-100). |
| --- | --- |
| How it's computed | Heat loss and insulation score computed per building. |
| How to read it | Amsterdam Universiteit: heat loss 46.8, insulation 55.4 — old building, classic retrofit candidate. Berliner: heat loss 25.6, insulation 86.5 — modern, no retrofit needed. |
| Why it matters | The cross-view of heat loss × insulation answers 'which building's retrofit ROI returns fastest'. |

V5 — Renovation Priority Matrix (Scatter)

Type: Scatter

| What it shows | X = Insulation Score; Y = HVAC Efficiency Score; colour saturation = Renovation Priority Color (numeric). |
| --- | --- |
| How it's computed | Per-building axes; priority = (1-insul/100) × (1-hvac_eff/100) — bad-bad = high priority. |
| How to read it | Bottom-left (low insulation + low HVAC eff) = immediate retrofit. Top-right = healthy, monitor. Berliner top-right (efficient); Amsterdam/Frankfurt bottom-left (retrofit now). |
| Why it matters | This scatter is the 'priority matrix' standard in engineering reports — the visual form of capex planning. |

How to talk about this page

'The portfolio HVAC share is 20% — low; but the Frankfurt hospital with its gas boiler produces 55% of the portfolio's HVAC carbon. Heat pump retrofit: capex €Z, Scope 1 → 0, ETS2 €Y/year saved + energy €X/year saved. Total payback 8-10 years. Failing to retrofit before EPBD 2030 risks the asset being stranded.'

Page 8 — IoT Monitoring (Real-Time)

Purpose of the page

Real-time operational monitoring. Live data from the BMS/IoT sensors: kW, zone comfort, CO₂, sensor health, alerts. The page a facility manager uses to 'see and respond instantly'.

Pipeline: Event Hub → Fabric EventStream → KQL Eventhouse (hot path) + Lakehouse (cold path). DAX v44.

Important architectural decision: sensor_type is a DIMENSION — not hardcoded. Each building shows only its connected sensors (BACnet/Modbus/MQTT adapter pattern, Phase 2 production-grade design).

Top band — KPI cards

Real-Time Building Power (96.5 kW ~ Above normal)

| What it shows | Last 15-minute average power draw. |
| --- | --- |
| How it's computed | MAX(timestamp_bldg_kw) WHERE bldg_id = selected. |
| How to read it | 96.5 kW — compare to baseline: 'Above normal' means 120%+ over baseline. Spike causes: HVAC trip, startup, equipment abnormality. |
| Why it matters | Real-time visibility is critical for demand-response programmes (peak shaving decisions must happen within 5 minutes). |

Zone Comfort Compliance (90% zones OK)

| What it shows | Real-time share of zones inside their setpoint range. |
| --- | --- |
| How it's computed | COUNT(zones WHERE temp BETWEEN setpoint±2°C AND CO2 < 1000) / total_zones × 100 |
| How to read it | 90% — good (target >85%). 10% out of range — could be HVAC trip, sensor fault, or genuine comfort issue. |
| Why it matters | Comfort non-compliance = complaints + tenant loss. The live metric for the energy-savings vs comfort balance. |

CO₂ Level (1873 ppm — IDA 4 Poor)

| What it shows | Real-time mean indoor CO₂ concentration. |
| --- | --- |
| How it's computed | AVG(co2_ppm) across all CO₂ sensors WHERE timestamp = latest. |
| How to read it | 1873 ppm — IDA 4 (EN 13779 standard: IDA 1 <800 / IDA 2 800-1000 / IDA 3 1000-1400 / IDA 4 >1400). Very poor — ventilation insufficient. |
| Why it matters | Elevated CO₂ harms cognitive performance (>1000 ppm), reducing learning/work productivity. Non-compliance with standards is also a legal risk. |

Active Alerts + Estimated Cost (237 Active — Est. €...)

| What it shows | Active high-severity alert count + their estimated daily € cost. |
| --- | --- |
| How it's computed | COUNT(active_alerts) + SUM(estimated_eur_cost_per_anomaly) |
| How to read it | 237 alerts is very high — either oversensitive system or a genuine fault. The € cost integration lets you see waste before the bill. |
| Why it matters | Anomaly-bound cost estimate (formula below): tells the engineer 'we're losing €X right now' and accelerates a finance decision. |

Anomaly Cost Logic (always shown as Est.):

cost_eur = duration_hours × power_waste_kw × grid_price_eur_per_kwh — HVAC_temp violation: 2-5 kW extra per °C deviation; CO₂ spike >1500 ppm: 1-3 kW extra ventilation; Power spike >120% baseline: actual excess kW. Grid price by country: DE €0.20/kWh, TR €0.14/kWh.

V1 — Sensor Uptime by Zone Matrix

Type: Matrix (zone × sensor_type)

| What it shows | Rows = zone (Floor 1 Zone 1 etc.); Columns = sensor_type (Bldg kW, Boiler %, CO₂, Fan RPM, Humidity, HVAC kW, HVAC T°, Light kW, Plug). |
| --- | --- |
| How it's computed | uptime = SUM(minutes_online) / SUM(minutes_in_period) × 100 |
| How to read it | Cells 93-94% — healthy. Below 90% indicates a sensor issue. An empty cell = sensor doesn't exist in that zone (sensor_type dimension is dynamic). Critical for MQTT vs BACnet-different buildings. |
| Why it matters | Sensor health = data quality = analytics trust. Below 80% uptime, analytics decisions become unreliable. |

V2 — Zone Anomaly Count — by Severity

Type: Stacked Horizontal Bar

| What it shows | Y = zone; X = alert count; stack: High/Medium/Low. |
| --- | --- |
| How it's computed | COUNT(alerts) GROUP BY zone, severity |
| How to read it | Floor 1 Zone 1: 206 alerts (total) — the hottest. Floor 2 Zone 3: 60 noticeable. Per-zone issue density. |
| Why it matters | This is 'hot spot' detection on the floor plan. A zone constantly producing alerts means either sensor calibration drift or a real HVAC issue. |

V3 — Building & HVAC Power — Last 24h

Type: Line Chart, 3 series

| What it shows | X = hour (last 24h); Y = kW; lines: Building Total (blue), HVAC (orange), Baseline (dashed grey). |
| --- | --- |
| How it's computed | Building total = SUM(zone_kw); HVAC = sub-metered; Baseline = 30-day average for the same hour. |
| How to read it | Blue line 120%+ above baseline = spike. HVAC line sudden rise (e.g. 08:00 startup) is normal; not declining at night (00-05) is an anomaly. |
| Why it matters | The 24-hour kW profile shows 'building rhythm'. It's the fastest visual for anomaly detection. |

V4 — Alert Table

Type: Table

| What it shows | Columns: Building, Zone, Sensor, Reading, Value, Unit, Severity, Recommended Action, Est. cost. |
| --- | --- |
| How it's computed | iot_anomaly_alerts (rule-based + signature-based detection). |
| How to read it | Example: B002 Plant Room boiler_eff 60.6% High → 'Boiler efficiency critical (<70%)'. B003 boiler_eff 95% Medium → 'Boiler efficiency declining'. |
| Why it matters | This table is the FM's 'work order' queue. With the Recommended Action you trigger direct response (team assignment, parts order, etc.). |

How to talk about this page

'The building is drawing 96.5 kW right now, 120% over baseline — a spike. CO₂ is 1873 ppm — IDA 4 Poor, ventilation insufficient; Floor 1 Zone 1 has 206 accumulated alerts. Boiler efficiency dropped to 60% — maintenance order needed. Estimated daily loss €47.'

Page 9 — Battery Strategy & ROI Simulation

Purpose of the page

The business case for a solar + battery investment. ROI, payback, CAPEX, and CO₂ avoided across 4 dispatch strategies (Self-Consumption, Peak-Shaving, Backup, Time-of-Use). EU Battery Regulation 2023/1670 compliance is also addressed here.

13 scenarios per building (LFP vs NMC × 4 strategies + actual). Pricing: DE off-peak €0.062 / peak €0.285 / demand charge €13.50/kW/month; AT/NL similar.

Top band — KPI cards

Annual Savings (€55,078.3)

| What it shows | Annual € savings for the selected building + strategy combination. |
| --- | --- |
| How it's computed | Σ(arbitrage_savings + demand_charge_avoided + self_consumption_increased) |
| How to read it | €55K/year for Hamburg Logistics on a Peak-Shaving strategy. Varies by strategy: Self-Consumption €X for B001, Peak-Shaving €Y for B003. |
| Why it matters | Annual savings is the primary input to payback and IRR. The loudest card in a sales pitch. |

Payback Period (7.9 yr)

| What it shows | How long it takes to recover the net investment (years). |
| --- | --- |
| How it's computed | CAPEX / annual_savings (simple); discounted version via IRR/NPV. |
| How to read it | 7.9 years — acceptable (10-year threshold). Goal: 8.1 ⚠ — at the edge. <5 years 'excellent', 5-10 'acceptable', >10 'reject'. |
| Why it matters | The payback threshold is the approve/reject decision for a battery investment. Bank financing usually requires <10 years. |

CO₂ Avoided (61.0 tCO₂/yr)

| What it shows | Annual carbon emissions avoided by the battery. |
| --- | --- |
| How it's computed | Σ(self_consumed_solar_kwh × grid_g_co2) — more solar used = less grid carbon. |
| How to read it | 61 tCO₂/year × €100 ETS2 = €6,100/year 'shadow value' savings. Cash + green premium together. |
| Why it matters | CO₂ avoided is critical to qualify under EU Taxonomy green investment criteria (~50%+ avoided required). |

Efficiency + EU (94.5%)

| What it shows | Battery round-trip efficiency + EU 2023/1670 compliance status. |
| --- | --- |
| How it's computed | round_trip_efficiency_percent × eu_compliant_boolean. LFP ~94%, NMC ~95%, NCA ~92%. |
| How to read it | 94.5% — LFP profile (CATL/BYD/Fluence). EU compliant ✅. NMC systems aren't always EU compliant. |
| Why it matters | Low round-trip efficiency = high heat loss = less saving. No EU compliance = cannot be sold/installed in the EU market (post-2024). |

V1 — Monthly Charge / Discharge

Type: Combo Bar+Line

| What it shows | X = month; bars: Charge kWh, Discharge kWh; line: PV Generation kWh. |
| --- | --- |
| How it's computed | Monthly aggregates; charge ~ PV generation in parallel. |
| How to read it | Charge peaks at PV generation peak (summer); discharge spikes in the evening + morning peaks. Seasonal pattern expected. |
| Why it matters | The visual test of whether the strategy 'works'. A flat discharge line = the strategy isn't dispatching (idle battery). |

V2 — Scenario Comparison Table

Type: Table

| What it shows | Columns: Building, Strategy, Battery kWh, CAPEX, Annual Savings, Payback, IRR, NPV, EU Compliant, Score. |
| --- | --- |
| How it's computed | gold_battery_simulation, 13 scenarios per building. |
| How to read it | Hamburg Peak-Shaving LFP 6,800 kWh CAPEX €960K — large battery, payback 1.7 years, IRR 63% (excellent). Hamburg Self-Consumption NMC just 400 kWh €54K — small, 25-year payback (poor). |
| Why it matters | The scenario comparison is the matrix for 'right strategy + right size'. The strongest table in a client pitch. |

V3 — ROI Gauge

Type: Radial Gauge

| What it shows | Min 0, Max 100; current 42 — 'Acceptable — review strategy'. |
| --- | --- |
| How it's computed | Composite score: payback (50%) + IRR (30%) + EU compliance (20%). |
| How to read it | 42 — 0-50 reject, 50-75 accept, 75-100 excellent. The strategy can be changed for the selection; selecting another scenario moves the gauge. |
| Why it matters | The ROI gauge gives a client or executive a one-glance answer on whether the investment is good or bad. Strong marketing pull. |

V4 — CAPEX vs PAYBACK (Scatter)

Type: Scatter (each point = a scenario)

| What it shows | X = CAPEX (€), Y = Payback (years), colour = strategy, size = annual savings. |
| --- | --- |
| How it's computed | Threshold lines: Max acceptable payback = 12, Good payback = 7. |
| How to read it | Berliner Self-Consumption 200 kWh LFP (reference point). Bottom-left (low CAPEX + short payback) = best-sellers. Top-right (high CAPEX + long payback) = reject. |
| Why it matters | The flight map of the investment decision. Pick a scenario and compare to others. |

V5 — 24h Battery Behavior by Strategy

Type: Multi-line + bars

| What it shows | X = hour (0-23); bars: Charge ↑ / Discharge ↓; lines: State of Charge (%), Price Index (100=avg). |
| --- | --- |
| How it's computed | Hourly simulation per strategy. |
| How to read it | Self-Consumption: charge during the day (PV peak), discharge in the evening. Peak-Shaving: charge before the 17-21 demand peak, discharge through it. ToU: charge at night off-peak (€0.062), sell during the day peak (€0.285). |
| Why it matters | This visual explains 'how the strategy works'. You can take a client through 4 different patterns to choose the right profile for them. |

EU Battery Regulation 2023/1670 — Critical Note

Post-January 2024, all batteries sold in the EU must include:

Carbon footprint label (Product Environmental Footprint, PEF)

State of Health (SoH) %

Cycle durability warranty

Recycled content % disclosure

B005 Frankfurt 400 kWh NMC Samsung — no EU compliance (missing carbon label). Marked red in the table; recommendation: replace with LFP CATL/BYD, which has the EU label.

How to talk about this page

'For Hamburg Logistics a Peak-Shaving LFP 6,800 kWh system — CAPEX €960K, annual saving €55K, payback 1.7 years, IRR 63%, CO₂ avoided 61 t/year. 94% round-trip in the European market, EU 2023/1670 compliant. A packaged investment recommendation for the client.'

Appendix A — Quick References

Units & conversions

| kWh/m²/day × 365 | = kWh/m²/year (annual EUI) |
| --- | --- |
| kWh elec × 0.40 | ≈ kgCO₂ (DE grid 2024, falling) |
| kWh gas × 0.20 | = kgCO₂ (natural gas, constant) |
| HDD/CDD base temperature | Heating 18°C, Cooling 22°C (ASHRAE) |
| Peak demand kW | × country demand charge €/kW/month × 12 = annual demand fee |
| Round-trip efficiency | discharge_kwh / charge_kwh — LFP 94%, NMC 95%, NCA 92% |

Standards / Regulations

| EPBD 2030 | EU Energy Performance of Buildings Directive — minimum class E for all buildings |
| --- | --- |
| CSRD | Corporate Sustainability Reporting Directive — annual carbon report |
| ETS2 | Emissions Trading System 2 — starts 2027, covers buildings, tCO₂ × €85-130 |
| CRREM | Carbon Risk Real Estate Monitor — pathway-based stranding year per asset |
| EU Battery Reg 2023/1670 | Carbon footprint label + SoH + cycle warranty + recycled content |
| EN 13779 IDA | Indoor air quality: IDA 1 <800 ppm, IDA 4 >1400 ppm CO₂ |
| ASHRAE 135 | BACnet/IP — building automation communication standard |
| IEC 61158 | Modbus TCP — industrial communication standard |
| ISO/IEC 20922 | MQTT 5.0 — IoT messaging protocol |
| IPMVP Option C | M&V baseline regression — retrofit verification standard |

DAX measure version map (summary)

| Pages 1-6 | DAX v10-v32 — base measures, slicers, KPI cards |
| --- | --- |
| Page 7 | v42 — EN labels + YoY/MoM trends (ACTIVE) |
| Page 8 | v44 — IoT real-time measures (zone, alert, cost) |
| Page 9 | v47 + v48 patch — 32 base measures + 4 fixes (locale, label, MonthYear) |

Architecture layers

| Bronze | Raw CSV / API / IoT EventStream — protocol-native data |
| --- | --- |
| Silver | Normalised + standard units — analytics-ready |
| Gold | Business logic tables — gold_kpi_daily, gold_hvac_analytics, gold_battery_dispatch, gold_iot_realtime, gold_compliance_results |
| Power BI | DirectLake mode, semantic model, DAX measures per page v34→v48 |

Persona — page usage

| Facility Manager | Daily: Pages 2 (profile), 3 (anomalies), 5 (occupancy), 8 (real-time IoT) |
| --- | --- |
| Energy Manager | Weekly: Pages 1 (overview), 3, 4 (forecast/recommendations), 6 (carbon), 7 (HVAC) |
| Consultant | Strategic: Pages 1, 4, 6, 7, 9 — generates investment proposals |
| CFO / Owner | Monthly: Page 1 (summary), 6 (carbon risk), 9 (investment ROI) |

— End —